## Job Summary
Site | Job Number | Test Date | Test Engineers
Holiday Inn Express Dublin City Centre | T0001639 | 45545 | Harry Willis, Ashley Allen
Damper Testing Summary | Number
Damper Type
Motorised | 121
Mechanical | 228
Intumescent | 0
Number of dampers located | 349
Number of dampers tested | 147
Number passed | 34
Number passed with issues | 114 | Fail
Number failed | 201 | Pass with issues
Number N/A | 0 | pass
Number installation passed | 41 | n/a
Number installation failed | 308
Fail Breakdown by Group | Number of Fails
Not installed per Specification | 124 | N
Installation quality unknown | 23
No access to damper | 82 | N
Firestopping problems | 13 | N
Other | 0
Total fail number may exceed total damper count as dampers may have more than one point of failure

## Asset Register
Damper Ref | Level | Location | Damper Pass, Fail or N/A | Installation Pass/Fail or Unknown | Damper Type | Damper Size | Duct Size | Damper Manufacturer | Damper Tested | Test Comments | Installed to Specification | Installation Comments | Access to Damper | Access Comments | Builders Hatch Size | Firestopping Integrity | Firestopping Comments | Damper Cleaned | Cleaning Comments
323 | G | Boh toilet | Passed With Issues | Fail | Mechanical | 500x500 | 450 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
324 | G | Boh toilet | Fail | Fail | Mechanical | Unknown | Unknown | Unknown | N |  | U | Unable to determine, impaired access | N | Services obstruction, refer to FRA |  | Y |  | N
325 | G | Boh toilet | Passed With Issues | Fail | Mechanical | 400x400 | 350 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
326 | G | Outside toilets | Passed With Issues | Fail | Mechanical | 400x400 | 400 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
327 | G | Riser by toilets | Fail | Fail | Mechanical | 400 | 400 | Unknown | N |  | U | Unable to determine, impaired access | N | Install spiral duct access door to suit duct |  | Y |  | N
328 | G | Riser by toilets | Passed With Issues | Fail | Motorised | 400x400 | 400 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
329 | G | Riser by toilets | Fail | Fail | Motorised | 400x400 | 400 | Action Air | N | No power. Qualified person to address | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
330 | G | Riser by toilet's | Passed With Issues | Fail | Motorised | 400x400 | 350 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
331 | G | Riser by toilets | Passed With Issues | Fail | Motorised | 400x400 | 350 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
332 | G | Hatch Outside toilet | Passed With Issues | Fail | Mechanical | 400x400 | 350 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
333 | G | Outside toilets | Passed With Issues | Fail | Mechanical | 400x400 | 400 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
334 | G | Riser by toilets | Passed With Issues | Fail | Mechanical | 400x400 | 400 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
335 | G | Riser by toilets | Passed With Issues | Fail | Mechanical | 300x300 | 300 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
336 | G | Male toilet | Passed With Issues | Fail | Mechanical | 400x400 | 400 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
337 | G | Hatch Outside toilet | Passed With Issues | Fail | Mechanical | 300x300 | 250 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
338 | G | Riser by disabled toilet | Fail | Fail | Mechanical | Unknown | Unknown | Unknown | N |  | U | Unable to determine, impaired access | N | Install builders hatch | Install 600x600 builders hatch | Y |  | N
339 | G | Female toilet | Passed With Issues | Fail | Mechanical | 400x400 | 400 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
340 | G | Reception office | Passed With Issues | Fail | Mechanical | 500x500 | 460 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
341 | G | Reception office | Passed With Issues | Fail | Mechanical | 250x250 | 200 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
342 | G | Reception office | Passed With Issues | Fail | Mechanical | 500x500 | 450 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
343 | G | Reception office | Fail | Fail | Mechanical | Unknown | Unknown | Unknown | N |  | U | Unable to determine, impaired access | N | Office safe obstruction unable to test damper |  | Y |  | N
344 | G | Reception office | Fail | Fail | Mechanical | 150 | 100 | Action Air | N |  | N | No breakaway joint, ammend installation | N | Duct to small to test damper replace |  | Y |  | N
345 | G | Reception office | Passed With Issues | Fail | Mechanical | 250x250 | 200 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
346 | G | Corridor to kitchen | Passed With Issues | Fail | Mechanical | 775x400 | 775x400 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
347 | G | Kitchen corridor | Passed With Issues | Fail | Mechanical | 550x550 | 500 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
348 | G | Corridor by kitchen | Passed With Issues | Fail | Motorised | 600x300 | 600x300 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
349 | G | Kitchen corridor | Passed With Issues | Fail | Mechanical | 350x350 | 300 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
172 | B | Carpark | Passed With Issues | Fail | Motorised | 750x350 | 700x300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
173 | B | Carpark | Passed With Issues | Fail | Motorised | 750x350 | 700x300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
174 | B | Plant room | Passed With Issues | Fail | Motorised | 200x200 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
175 | B | Plant room | Passed With Issues | Fail | Motorised | 400x400 | 350 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
176 | B | Plant room | Passed With Issues | Fail | Motorised | 200x200 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
177 | B | Plant room | Passed With Issues | Fail | Motorised | 200x200 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
178 | B | Plant room | Passed With Issues | Fail | Motorised | 200x200 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
179 | B | Plant room | Passed With Issues | Fail | Motorised | 200x200 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
180 | B | Plant room | Passed With Issues | Fail | Motorised | 200x200 | 150 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
191 | B | Tank room | Passed With Issues | Fail | Motorised | 400x400 | 350 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
192 | B | Tank room | Passed With Issues | Fail | Mechanical | 300x300 | 250 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
193 | B | Tank room | Passed With Issues | Fail | Motorised | 300x300 | 250 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
194 | B | Tank room | Passed With Issues | Fail | Motorised | 300x300 | 250 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
195 | B | Outside toilets by meeting rooms | Fail | Fail | Mechanical | 300x300 | 250 | Action Air | N |  | N | Unable to determine, impaired access | N | Install builders hatch | Increase builders hatch size to 600x300 | Y |  | N
196 | B | Outside toilets by meeting rooms | Passed With Issues | Fail | Mechanical | 250x250 | 200 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
197 | B | Above single door to meeting rooms | Passed With Issues | Fail | Motorised | 200x200 | 150 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
198 | B | Above single door to meeting rooms | Passed With Issues | Fail | Motorised | 200x200 | 150 | Action Air | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
1 | 6 | Room 610 | Fail | Fail | Mechanical | 100 | 100 | Unknown | N | Replace damper, closed and unable to re-set | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | Y
2 | 6 | Room 630 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
3 | 6 | Room 631 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | Y
10 | 6 | Riser by 614 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
11 | 6 | Riser by 613 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
12 | 6 | Riser by 616 | Fail | Pass | Motorised | 300 | 300 | Unknown | N | Damper will not fully close, replace | Y |  | Y |  |  | Y |  | Y
13 | 6 | Riser by 618 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
14 | 6 | Riser by 611 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
15 | 6 | Riser by 620 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
16 | 6 | Riser by 609 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
17 | 6 | Riser by 622 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
18 | 6 | Riser by 624 | Passed With Issues | Pass | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
19 | 6 | Riser by 625 | Passed With Issues | Pass | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
20 | 6 | Riser by 605 | Passed With Issues | Pass | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
21 | 6 | Riser by 626 | Passed With Issues | Pass | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
22 | 6 | Riser by 628 | Passed With Issues | Pass | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
23 | 6 | Riser by 628 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
24 | 6 | Riser by 629 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
25 | 6 | Riser by 604 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
26 | 6 | Riser by 631 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
27 | 6 | Riser by 602 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
37 | 6 | Room 602 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N
38 | 6 | Room 606 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
50 | 6 | Riser by 526 | Passed With Issues | Fail | Motorised | 300 | 400 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
152 | 6 | Room 622 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
153 | 6 | Room 612 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
164 | 6 | Room 604 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
165 | 6 | Room 605 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
166 | 6 | Room 607 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
167 | 6 | Room 608 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
168 | 6 | Room 609 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
169 | 6 | Room 611 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
170 | 6 | Room 613 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
171 | 6 | Room 614 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
181 | 6 | Room 616 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
182 | 6 | Room 617 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
183 | 6 | Room 618 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
184 | 6 | Room 619 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
185 | 6 | Room 621 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
186 | 6 | Room 623 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
187 | 6 | Room 626 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
188 | 6 | Room 625 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
189 | 6 | Room 627 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
190 | 6 | Room 628 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
278 | 6 | Room opposite 627 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
279 | 6 | Riser in room by 625 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N
285 | 6 | Outside 624 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | N | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N
286 | 6 | Outside 624 | Fail | Fail | Mechanical | 100 | 100 | Unknown | N |  | U | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N
298 | 6 | Room 614 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
299 | 6 | Riser in 614 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
304 | 6 | Room 631 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
305 | 6 | Room 601 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
306 | 6 | Room 620 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
4 | 5 | Room 501 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | Y
5 | 5 | Room 514 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | Y
6 | 5 | Riser in 514 | Passed With Issues | Fail | Motorised | 250 | 250 | Other | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
7 | 5 | Room 517 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
8 | 5 | Room 518 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
9 | 5 | Room 521 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
39 | 5 | Riser by 514 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
40 | 5 | Riser by 613 | Pass | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
41 | 5 | Riser by 517 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
42 | 5 | Riser by 518 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
43 | 5 | Riser by 511 | Passed With Issues | Fail | Motorised | 300 | 390 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
44 | 5 | Riser by 521 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
45 | 5 | Riser by 509 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
46 | 5 | Riser by 522 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
47 | 5 | Riser by 507 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
48 | 5 | Riser by 525 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
49 | 5 | Riser by 506 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
51 | 5 | Riser by 528 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
52 | 5 | Riser by 528 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
53 | 5 | Riser by 529 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
54 | 5 | Riser by 504 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
55 | 5 | Riser by 530 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
56 | 5 | Riser by 501 | Passed With Issues | Fail | Motorised | 300 | 300 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
144 | 5 | Room 502 | Passed With Issues | Fail | Mechanical | 100 | 100 | Other | Y |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | Y
154 | 5 | Room 526 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
155 | 5 | Room 527 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | N | Unable to locate damper, install 100mm stik | N |  |  | N |  | N
156 | 5 | Room 505 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
157 | 5 | Room 503 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
158 | 5 | Room 531 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
199 | 5 | Room 504 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
200 | 5 | Room 525 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
201 | 5 | Room 507 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
202 | 5 | Room 509 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
203 | 5 | Room 511 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
204 | 5 | Room 512 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
205 | 5 | Room 516 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
206 | 5 | Room 520 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
207 | 5 | Room 522 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | N | Damper missing, install 100mm flakt | N |  |  | N |  | N
208 | 5 | Room 523 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
209 | 5 | Room 528 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
210 | 5 | Room 530 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
280 | 5 | Room opposite 529 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
281 | 5 | Room by 525 | Passed With Issues | Fail | Motorised | 200 | 200 | Unknown | N | No power. Qualified person to address | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
287 | 5 | Outside 524 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N
288 | 5 | Outside 524 | Fail | Fail | Mechanical | 100 | 100 | Unknown | N |  | U | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N
300 | 5 | Room 513 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
307 | 5 | Room 510 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
308 | 5 | Room 508 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
309 | 5 | Room 506 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
315 | 5 | Room 515 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | N | Unable to determine, impaired access | N | Room occupied, unable to access |  | N | Unable to determine, impaired access | N
318 | 5 | Room 515 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | Room occupied, unable to access |  | N | Unable to determine, impaired access | N
319 | 5 | Room 519 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | Room occupied, unable to access |  | N | Unable to determine, impaired access | N
28 | 4 | Room 405 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
29 | 4 | Room 411 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
30 | 4 | Room 422 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
31 | 4 | Room 408 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
32 | 4 | Room 425 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
33 | 4 | Room 426 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
34 | 4 | Room 428 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
35 | 4 | Room 430 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
36 | 4 | Room 434 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
60 | 4 | Riser in 314 | Passed With Issues | Fail | Motorised | 200 | 200 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
97 | 4 | Riser by 414 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
98 | 4 | Riser by 412 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
99 | 4 | Riser by 417 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
100 | 4 | Riser by 418 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
101 | 4 | Riser by 411 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
102 | 4 | Riser by 421 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
103 | 4 | Riser by 408 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
104 | 4 | Riser by 422 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
105 | 4 | Riser by 407 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
106 | 4 | Riser by 425 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
107 | 4 | Riser by 405 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
108 | 4 | Riser by 427 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
109 | 4 | Riser by 429 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
110 | 4 | Riser by 432 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
111 | 4 | Riser by 430 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
112 | 4 | Riser by 404 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
113 | 4 | Riser by 433 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
114 | 4 | Riser by 401 | Passed With Issues | Fail | Motorised | 250 | 250 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
132 | 4 | Riser by 308 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
140 | 4 | Riser by 330 | Pass | Pass | Motorised | 200 | 290 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
159 | 4 | Room 406 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
160 | 4 | Room 423 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
161 | 4 | Room 419 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
162 | 4 | Room 417 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
211 | 4 | Room 401 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
212 | 4 | Room 402 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
213 | 4 | Room 403 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
214 | 4 | Room 404 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
215 | 4 | Room 410 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
216 | 4 | Room 412 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
217 | 4 | Room 413 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
218 | 4 | Room 418 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
219 | 4 | Room 420 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
220 | 4 | Room 427 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
221 | 4 | Room 429 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
222 | 4 | Room 432 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | N | Damper missing, install 100mm flakt | N |  |  | N |  | N
223 | 4 | Room 433 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
282 | 4 | Room opposite 432 | Fail | Fail | Motorised | 250 | 259 | Unknown | N | No power. Qualified person to address | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N
289 | 4 | Outside 424 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | Services obstruction, refer to FRA |  | Y |  | N
290 | 4 | Outside 424 | Fail | Fail | Mechanical | 100 | 100 | Unknown | N |  | U | Unable to determine, impaired access | N | Services obstruction, refer to FRA |  | Y |  | N
310 | 4 | Room 407 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
311 | 4 | Room 421 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
312 | 4 | Room 416 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
314 | 4 | Room 414 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | Damper out of reach, refer to FRA |  | N | Unable to determine, impaired access | N
316 | 4 | Room 409 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | Room occupied, unable to access |  | N | Unable to determine, impaired access | N
317 | 4 | Room 431 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | Room occupied, unable to access |  | N | Unable to determine, impaired access | N
57 | 3 | Room 305 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
58 | 3 | Room 306 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
59 | 3 | Room 314 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
61 | 3 | Room 315 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
62 | 3 | Room 319 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
63 | 3 | Room 321 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
64 | 3 | Room 330 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
65 | 3 | Room 331 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
66 | 3 | Room 331 | Fail | Fail | Mechanical | 100 | 100 | Flakt | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
67 | 3 | Room 334 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
118 | 3 | Riser by 218 | Passed With Issues | Fail | Motorised | 100 | 100 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
126 | 3 | Riser by 314 | Passed With Issues | Fail | Motorised | 200 | 200 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
127 | 3 | Riser by 313 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
128 | 3 | Riser by 317 | Fail | Pass | Motorised | 300 | 300 | Unknown | N | Replace damper, closed and unable to re-set | Y |  | Y |  |  | Y |  | N
129 | 3 | Riser by 311 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
130 | 3 | Riser by 318 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
131 | 3 | Riser by 320 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
133 | 3 | Riser by 322 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
134 | 3 | Riser by307 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
135 | 3 | Riser by 325 | Pass | Pass | Motorised | 200 | 200 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
136 | 3 | Riser by 305 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
137 | 3 | Riser by 327 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
138 | 3 | Riser by 329 | Passed With Issues | Fail | Motorised | 200 | 200 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
139 | 3 | Riser by 322 | Pass | Pass | Motorised | 200 | 200 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
141 | 3 | Riser by 304 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
142 | 3 | Riser by 333 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
143 | 3 | Riser by 301 | Pass | Pass | Motorised | 300 | 300 | Unknown | Y |  | Y |  | Y |  |  | Y |  | Y
163 | 3 | Room 329 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
224 | 3 | Room 303 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
225 | 3 | Room 304 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
226 | 3 | Room 307 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
227 | 3 | Room 308 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N
228 | 3 | Room 310 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
229 | 3 | Room 311 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
230 | 3 | Room 312 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
231 | 3 | Room 313 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
232 | 3 | Room 316 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
233 | 3 | Room 317 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
234 | 3 | Room 318 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
235 | 3 | Room 320 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
236 | 3 | Room 322 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
237 | 3 | Room 323 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
238 | 3 | Room 325 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
239 | 3 | Room 327 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
240 | 3 | Room 328 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
241 | 3 | Room 332 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | N | Damper missing, install 100mm flakt | N |  |  | N |  | N
242 | 3 | Room 333 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
283 | 3 | Room opposite 332 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
291 | 3 | Outside 324 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N
292 | 3 | Outside 324 | Fail | Fail | Mechanical | 100 | 100 | Unknown | N |  | U | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N
297 | 3 | Room 301 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
301 | 3 | Room 309 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
313 | 3 | Room 326 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | Room occupied, unable to access |  | N | Unable to determine, impaired access | N
320 | 3 | Room 301 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | Room occupied, unable to access |  | N | Unable to determine, impaired access | N
321 | 3 | Room 302 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | Room occupied, unable to access |  | N | Unable to determine, impaired access | N
68 | 2 | Roon 203 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
69 | 2 | Room 204 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
70 | 2 | Room 205 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
71 | 2 | Room 229 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
72 | 2 | Room 206 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
73 | 2 | Room 226 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
74 | 2 | Room 208 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
75 | 2 | Room 212 | Fail | Fail | Mechanical | 100 | 100 | Other | N | Replace damper, closed and unable to re-set | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
76 | 2 | Room 215 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
77 | 2 | Room 218 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
78 | 2 | Room 219 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
79 | 2 | Room 221 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
80 | 2 | Room 222 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
81 | 2 | Room 223 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N
82 | 2 | Room 225 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
83 | 2 | Riser in 225 | Passed With Issues | Fail | Motorised | 100 | 100 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
84 | 2 | Room 227 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
85 | 2 | Room 230 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
86 | 2 | Room 234 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
115 | 2 | Riser by 214 | Passed With Issues | Fail | Motorised | 100 | 100 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch too far from damper
116 | 2 | Riser by 212 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
117 | 2 | Riser by 217 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
119 | 2 | Riser by 211 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
120 | 2 | Riser by 221 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
121 | 2 | Riser by 208 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
122 | 2 | Riser by 222 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
123 | 2 | Riser by 207 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
124 | 2 | Riser by 225 | Passed With Issues | Fail | Motorised | 100 | 100 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
125 | 2 | Riser by 205 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
145 | 2 | Riser by 227 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
146 | 2 | Riser by 229 | Passed With Issues | Fail | Motorised | 100 | 100 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
147 | 2 | Riser by 232 | Passed With Issues | Fail | Motorised | 100 | 100 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
148 | 2 | Riser by 230 | Passed With Issues | Fail | Motorised | 100 | 100 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
149 | 2 | Riser by 204 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
150 | 2 | Riser by 233 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
151 | 2 | Riser by 201 | Passed With Issues | Fail | Motorised | 150 | 150 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
243 | 2 | Room 201 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
244 | 2 | Room 202 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
245 | 2 | Room 208 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
246 | 2 | Room 209 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
247 | 2 | Room 210 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
248 | 2 | Room 211 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
249 | 2 | Room 217 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
250 | 2 | Room 214 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
251 | 2 | Riser in 214 | Passed With Issues | Fail | Motorised | 100 | 100 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | N | Hatch to far from damper
252 | 2 | Room 216 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
253 | 2 | Room 228 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
254 | 2 | Rook 231 | Fail | Pass | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
255 | 2 | Room 233 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
270 | 2 | Room 120 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
284 | 2 | Room opposite 232 | Passed With Issues | Fail | Motorised | 100 | 100 | Unknown | Y |  | N | No breakaway joint, ammend installation | Y |  |  | Y |  | Y
293 | 2 | Outside 224 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N
294 | 2 | Outside 224 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | U | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N
302 | 2 | Room 213 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
303 | 2 | Room 220 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
322 | 2 | Room 232 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N
87 | 1 | Room 101 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
88 | 1 | Room 103 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N
89 | 1 | Room 107 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
90 | 1 | Room 112 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
91 | 1 | Room 119 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
92 | 1 | Room 126 | Fail | Fail | Mechanical | 100 | 100 | Other | N | Replace damper, closed and unable to re-set | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
93 | 1 | Room 128 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
94 | 1 | Room 132 | Pass | Pass | Mechanical | 100 | 100 | Other | Y |  | Y |  | Y |  |  | Y |  | Y
95 | 1 | Room 133 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
96 | 1 | Room 134 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
256 | 1 | Room 102 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
257 | 1 | Room 104 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
258 | 1 | Room 105 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
259 | 1 | Room 106 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
260 | 1 | Room 108 | Pass | Pass | Mechanical | 100 | 100 | Flakt | Y |  | Y |  | Y |  |  | Y |  | Y
261 | 1 | Room 109 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
262 | 1 | Room 110 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
263 | 1 | Room 111 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
264 | 1 | Room 113 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
265 | 1 | Room 114 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
266 | 1 | Room 115 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
267 | 1 | Room 116 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
268 | 1 | Room 117 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
269 | 1 | Room 118 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
271 | 1 | Room 121 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
272 | 1 | Room 123 | Fail | Fail | Mechanical | 100 | 100 | Other | N | Damper closed | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
273 | 1 | Room 125 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
274 | 1 | Room 127 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N
275 | 1 | Room 129 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
276 | 1 | Room 130 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
277 | 1 | Room 131 | Fail | Fail | Mechanical | 100 | 100 | Other | N |  | Y |  | N | Unable to remove damper from duct, further investigation required |  | Y |  | N | Unable to remove
295 | 1 | Outside 124 | Fail | Fail | Mechanical | 100 | 100 | Unknown | N |  | U | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N
296 | 1 | Outside 124 | Fail | Fail | Mechanical | 100 | 100 | Unknown | N |  | U | Unable to determine, impaired access | N | No duct access door or space, install a removable duct section |  | Y |  | N

## Asset Register Notes
Column Heading | Note
Damper Ref | Number or alpha-numeric
Level | The floor where the damper islocated
Location | The place where the damper is to be found
Damper Pass, Fail or N/A | The damper will be passed if it functions as per design. Passed with issues if it functions as per design but the installation fails and failed if it does not function as per design
NOTE | If the damper has been passed with issues or failed it will appear in red font. It is the responsibility of the building owner/operator to rectify these defects immediately (ref; BS 9999 Annex W, W.1. Note 1)
Installation Pass/Fail or Unknown | The installation will be passes if the damper is installed to manufacturers specification and the firestopping is correctly installed. If either of these conditions are not met, the installation will be failed
NOTE | If the installation has been failed it will appear in red font. It is the responsibility of the building owner/operator to rectify these defects immediately (ref; BS 9999 Annex W, W.1. Note 1)
Damper Type | Fuseable (also called link or mechanical), motorised (also called electronic or automatic) or intumescent (which are single use dampers)
Damper Size | Self explanatory
Duct Size | Self explanatory
Damper Manufacturer | Self explanatory
Damper Tested | Y if the damper has been tested, N if not
Test Comments | Pertinent comments relating to the test
Installed to Specification | Y if the damper has been installed as per the manufacturers specification, N if not
Installation Comments | Pertinent comments relating to the installation
Access to Damper | Y if the damper is freely accesible to test N if not
Access Comments | Pertinent comments relating to the acessability
Builders Hatch Size | If a builders hatch is required to gain access, the recommended size will be stated here
Firestopping Integrity | Y if the firestopping integrity is good, N if compromised
Firestopping Comments | Pertinent comments relating to the firectopping repairs that are required (if any)
Damper Cleaned | Y if the damper has been cleaned, N if not
Cleaning Comments | Pertinent comments relating to the cleaning
General Comments | Note
Refer to FRA | The Fire Risk Assesor (FRA) should be consulted to seek a solution to the problem
Ghost damper | The damper is not situated within a fire compartment and should be removed
Dampers inspected but not tested | The damper has been visually inspected, usually by borescope, but due to access problems has not been tested. The inspection verifies the presence or absence of the damper only
Single Use Fire Dampers | Intumescent dampers and some mechanical dampers are single use only and thus cannot be tested.