## Sheet1
ROUTINE MAINTENANCE SERVICE
SULZER PUMPS WASTEWATER IRELAND
ORDER NO. |  |  | 870119 | [7 empty] | RIVERVIEW BUSINESS PARK
NEW NANGOR ROAD, DUBLIN 12
TEL 01 4608888 FAX 01 4608889
RMS Number |  |  | 1498 08 18 |  |  |  | Building Code
Client |  |  | QIUNNDOWNES
Service Date |  |  | 2023-02-28 |  |  |  | Call out by |  | CLIENT / |  |  | CONTACT
Site address |  |  | HOLIDAY INN EXPRESS
28-32 OCONNELL STREET UPPER , DUBLIN
Contact |  |  | CAOIMHE
Tel |  |  | 01 4242424 |  |  |  | E-Mail
Issue Invoice to
System Details
Routine |  |  |  | Emergency |  |  |  | Warranty |  |  |  | RMS |  | X
Pump Qty |  | 2 |  | Sump Depth |  | 3 METRE |  | Power |  | 400 V |  | Medium |  | FOUL
Level control |  | FLOATS X 4 |  |  |  | Control panel | BPC PANEL |  |  |  | Priority
Pump Type |  | XFP 80C CB1.1 PE 13/6
Serial Number |  | 399290 |  |  | Hrs | N/A |  | Serial Number |  | 399289 |  |  | Hrs | N/A
Pump No.1 |  |  |  |  | Run |  |  | Pump No.2 |  |  |  |  | Run
Application |  | FOUL PUMP STATION LOCATED IN TANK ROOM
Description
Service Report Details
Pump No.1 |  | PUMP CHECKED AND TESTED ,MOTOR INSULATION OK ,OIL OK ,CABLE OK , HYDRAULICS OK ,PEDESTAL SEAL INTACT.
PUMP OPERATING CORRECTLY .
Stator Resis Ω |  | 550 |  | DI Resis Ω |  | 550 | Cable X or OK |  | OK | Lifting Chain |  | y | Certified Y or N |  | y
Pump No.2 |  | PUMP CHECKED AND TESTED ,MOTOR INSULATION OK ,OIL OK ,CABLE OK , HYDRAULICS OK ,PEDESTAL SEAL INTACT.
PUMP OPERATING CORRECTLY .
Stator Resis Ω |  | 550 |  | DI Resis Ω |  | 550 | Cable X or OK |  | OK | Lifting Chain |  | y | Certified Y or N |  | y
Control Panel |  | ALL TERMINALS SECURE AND LAMPS AND TRIPS WORKING OK .
Sump condition |  | CRUST BUILD UP IN TANK ,TO BE CLEANED OUT ASAP TO PREVENT FALSE ALARMS .
Level Control |  | FLOATS TESTED AND CHECKED .ALL OK .
Valves
Fault Analysis
|  | OK | Equipment OK |  | X | Requires Attention
Estimated Cost Details
Part No |  |  |  | Description | [5 empty] | Qty |  |  | Nett Price Subtotal
RMS Service
Service Engineer |  |  | MICHAEL BROWNE / IGOR KITTEL |  |  |  | On Time |  |  | Off Time
Clients Signature | [6 empty] | Date | 2023-02-28