Holiday inn periodic inspection

Every swa in building is not earthed



Every room that was tested none of the bedside lights had protection for the connections



All service lift areas on all floors electrical outlets back box is not earthed



Distribution board in coffee shop neutral bar mounted on wood in the board



Large holes in distribution board for heating controls in plant room and gland has no lock ring



Distribution board in car park has no blanks



In basement car park cables not supported



Air conditioning area on 1st floor isolator held on by insulating tape



Car park in basement cable thrown across



Basement bottom of stairs connections left bare on ceiling

